## AnläggProvProgram
H2SO4
[8 empty] | 19.998 |  | m3/h |  |  |  | 14.6966 |  | l/h
| Input values | Output values |  | NaOH | [9 empty] | 1175.8466 |  | g/m3
Raw water |  |  |  | 19.9239 |  | l/h |  | 3.9996 |  | kg N/h
Flow of inlet water, kg/s | 5.555 | 19.998 | m3/h | [7 empty] | H2SO4 | [5 empty] | To final pH adjustment
Ammonia concentration, mg N/l | 200 | 14.2857 | mM | [6 empty] | 6.1217 |  | l/h | [5 empty] | 0.42941 |  | l/h | 34.3566
Bicarbonate concentration, mg HCO3/l | 610 | 10 | mM | [6 empty] | 489.781 |  | g/m3 | [5 empty] | 34.3566 |  | g/m3
Reagents
Concentration of sulphuric acid g/l H2SO4 | 1600 | [13 empty] | To absorber
Concentration of sodium hydroxide, g/l NaOH | 600 | [13 empty] | 8.1455 |  | l/h
Concentration of ferric chloride, g/l FeCl3 | 300 |  |  | 19.1661 |  | l/h |  |  |  |  | 50 |  | g/m3 |  | 651.709 |  | g/m3
FeCl3
Pretreatment | [10 empty] | 3.333 |  | l/h
Titration pH in acidification |  | 4.175 | pH
pH in stripper inlet | 3 |  | pH
Concentration of H2CO3 in acidified water, mM |  | 9.9955 | mM |  |  |  |  | 10.5 |  | pH
Concentration of bicarbonate in acidified water, mM |  | 0.0044688 | mM
Removal efficiency for CO2 stripper | 99.96%
Concentration of H2CO3 in aerated water, mM |  | 0.0044688 | mM | [7 empty] | Sludge
Concentration of bicarbonate in aerated water, mM |  | 0.0044688 | mM
Sulphuric acid consumption |  | 6.1217 | l/h
Specific dosage of FeCl3 (100%) g/m3 | 50 | 0.30826 | mM
Dosage flow of FeCl3 |  | 3.333 | l/h | 0.7578 |  | l/h
[8 empty] | 20 |  | °C
Titration pH in alkalisation |  | 10.7275 | [5 empty] | 11 |  | pH
Chosen pH value for precipitation | 10.5
Concentration of NH3 |  | 13.4378 | mM
Concentration of NH4 |  | 0.84787 | mM
Sodium hydroxide consumption: |  | 14.376 | mM | [10 empty] | 0.27592 |  | kg N/h
due to H2CO3 |  | 0.0089377 | mM
due to HCO3 |  | 0.0044688 | mM
due to NH3 |  | 13.4378 | mM |  | H2SO4
due to FeCl3 |  | 0.92478 | mM
Dosage flow of sodium hydroxide |  | 19.1661 | l/h | 0.42941 |  | l/h
Precipitation of CaCO3 |  | 0.0089377 | mM | 34.3566 |  | g/m3
Precipitation of Fe(OH)3 |  | 0.30826 | mM | [10 empty] | 22 |  | °C
Adjustment of pH before NH3 stripper | 11
Dosage flow of additional sodium hydroxide |  | 0.7578 | [8 empty] | 884.4671 |  | kW
Heating and heat recovery
Temperature of raw water °C | 20 | [6 empty] | 58 | °C
Temperature in stripper °C | 60
Heat recovery in heat exchanger, % | 95%
Heat recovered |  | 884.4671 | kW
Net heat losses in stripper & absorber, kW | 1 |  | kW | [7 empty] | 47.5509 |  | kW
Heat addition in external heater |  | 47.5509 | kW
Ammonia stripping | [7 empty] | 60.043 |  | °C
Removal efficiency of NH3 + NH4 | 93.1%
Stripping efficiency of NH3 |  | 94.96%
Outlet concentration of NH3-N + NH4-N |  | 13.7974 | mg/l
Removed NH3 |  | 73.8825 | mmol/s
Production of ammonium sulfate (100%) |  | 4.8762 | g/s
Number of available transfer units in desorber
Used transfer units in desorber
Slope of equilibrium line mol/mol / mol/mol |  | 3.9085
Gas flow m3/s; | 4 | 146.422 | mol/s
mV/L in stripper |  | 1.8544
Catchment efficiency of ammonia in absorber |  | 95.51% |  |  |  |  | 200 |  | mgN/l
Number of available transfer units in absorber | 3 | [5 empty] | 14.2857 |  | mM
Used transfer units in absorber |  | 3.0009 | [8 empty] | 0.022784 |  |  | mmol N/mol gas
Concentration of ammonium sulphate, weight % | 40% | 3.0303 | M
Entrainment of ammonium sulphate mg droplets/m3 gas | 20 |  | mg/m3
Entrainment rate |  | 0.48485 | mmol N/s
Ammonia after absorption mmole NH3/mole gas |  | 0.022784 | mmol/mol | [7 empty] | 4 |  | m3/s
due to nonabsorbed NH3, mmol/mol gas |  | 0.019473 | mmol/mol | [7 empty] | 146.422 |  | mol /s
due to entrainment, mmol/mol gas |  | 0.0033113 | mmol/mol
Ammonia conc in gas from stripper, mmol/mol gas |  | 0.5079 | mmol/mol
Equilibrium conc of NH3 above ammonium sulfate sol |  | 2.137e-06 | mmol/mol | [7 empty] | 0.45801 | [7 empty] | H2SO4
pH value in absorber | 4 | [9 empty] | mmol N/mol gas
Driving conc difference in top of absorber (gas) |  | 0.022782 | mmol/mol |  |  |  | 60 |  | °C | [7 empty] | 8.1455 |  | l/h
Driving conc difference in bottom of absorber (gas) |  | 0.45801 | mmol/mol |  |  |  | 13.7974 |  | mg N/l | [7 empty] | 651.709 |  | g/m3
Equilibrium conc of NH3 in top of stripper |  | 0.98538 | mmol/mol |  |  |  | 0.98553 |  | mM
NH3 (g) conc in top of stripper |  | 0.52737 | mmol/mol
Driving conc difference in top of stripper (gas) |  | 0.45801 | mmol/mol
Equilibrium conc of NH3 in bottom of stripper |  | 0.036298 | mmol/mol | [5 empty] | Difference: |  |  | -0.00091555
Driving conc difference in bottom of stripper (gas) |  | 0.013514 | mmol/mol | [5 empty] | absorber
Available transfer units in stripper | 4
Used transfer units in stripper |  | 3.9994 | [6 empty] | Difference |  |  | 0.00057523
pH value after stripper |  | 9.7025 | pH | [5 empty] | stripper
Sulphuric acid consumption in absorber |  | 8.1455 | l/h
Final pH adjustment
pH after adjustment | 7 |  | pH
Sulphuric acid consumption in final pH adjustment |  | 0.42941 | l/h
Note on A38: Choose 11-11,5
Stripper
Precipitation
Sedimentation
Sand filter
Carbon filter
Heat exch.
Heater.
NH3 Stripper
NH3 Absorber

## Design Tool
H2SO4
[8 empty] | 19.98 |  | m3/h |  |  |  | 14.682 |  | l/h
| Input values | Output values |  | NaOH | [9 empty] | 1175.7384 |  | g/m3
Raw water |  |  |  | 20.1605 |  | l/h |  | 3.996 |  | kg N/h
Flow of inlet water, kg/s | 5.55 | 19.98 | m3/h | [7 empty] | H2SO4 | [5 empty] | To final pH adjustment
Ammonia concentration, mg N/l | 200 | 14.2857 | mM | [6 empty] | 6.1161 |  | l/h | [5 empty] | 0.69858 |  | l/h | 55.942
Bicarbonate concentration, mg HCO3/l | 610 | 10 | mM | [6 empty] | 489.781 |  | g/m3 | [5 empty] | 55.942 |  | g/m3
Reagents
Concentration of sulphuric acid g/l H2SO4 | 1600 | [13 empty] | To absorber
Concentration of sodium hydroxide, g/l NaOH | 600 | [13 empty] | 7.8673 |  | l/h
Concentration of ferric chloride, g/l FeCl3 | 300 |  |  | 19.4034 |  | l/h |  |  |  |  | 50 |  | g/m3 |  | 630.0154 |  | g/m3
FeCl3
Pretreatment | [10 empty] | 3.33 |  | l/h
Titration pH in acidification |  | 4.175 | pH
pH in stripper inlet | 3 |  | pH
Concentration of H2CO3 in acidified water, mM |  | 9.9955 | mM |  |  |  |  | 10.5 |  | pH
Concentration of bicarbonate in acidified water, mM |  | 0.0044688 | mM
Removal efficiency for CO2 stripper | 99%
Concentration of H2CO3 in aerated water, mM |  | 0.1 | mM | [7 empty] | Sludge
Concentration of bicarbonate in aerated water, mM |  | 0.0044688 | mM
Sulphuric acid consumption |  | 6.1161 | l/h
Specific dosage of FeCl3 (100%) g/m3 | 50 | 0.30826 | mM
Dosage flow of FeCl3 |  | 3.33 | l/h | 0.75712 |  | l/h
[8 empty] | 10 |  | °C
Titration pH in alkalisation |  | 10.7275 | [5 empty] | 11 |  | pH
Chosen pH value for precipitation | 10.5
Concentration of NH3 |  | 13.4378 | mM
Concentration of NH4 |  | 0.84787 | mM
Sodium hydroxide consumption: |  | 14.5671 | mM | [10 empty] | 0.39951 |  | kg N/h
due to H2CO3 |  | 0.2 | mM
due to HCO3 |  | 0.0044688 | mM
due to NH3 |  | 13.4378 | mM |  | H2SO4
due to FeCl3 |  | 0.92478 | mM
Dosage flow of sodium hydroxide |  | 19.4034 | l/h | 0.69858 |  | l/h
Precipitation of CaCO3 |  | 0.10447 | mM | 55.942 |  | g/m3
Precipitation of Fe(OH)3 |  | 0.30826 | mM | [10 empty] | 12.5 |  | °C
Adjustment of pH before NH3 stripper | 11
Dosage flow of additional sodium hydroxide |  | 0.75712 | [8 empty] | 1104.5887 |  | kW
Heating and heat recovery
Temperature of raw water °C | 10 | [6 empty] | 57.5 | °C
Temperature in stripper °C | 60
Heat recovery in heat exchanger, % | 95%
Heat recovered |  | 1104.5887 | kW
Net heat losses in stripper & absorber, kW | 1 |  | kW | [7 empty] | 59.1363 |  | kW
Heat addition in external heater |  | 59.1363 | kW
Ammonia stripping | [7 empty] | 60.043 |  | °C
Removal efficiency of NH3 + NH4 | 90%
Stripping efficiency of NH3 |  | 91.8%
Outlet concentration of NH3-N + NH4-N |  | 19.9956 | mg/l
Removed NH3 |  | 71.3589 | mmol/s
Production of ammonium sulfate (100%) |  | 4.7097 | g/s
Number of available transfer units in desorber
Used transfer units in desorber
Slope of equilibrium line mol/mol / mol/mol |  | 3.9085
Gas flow m3/s; | 4 | 146.422 | mol/s
mV/L in stripper |  | 1.8561
Catchment efficiency of ammonia in absorber |  | 97.48% |  |  |  |  | 200 |  | mgN/l
Number of available transfer units in absorber | 3 | [5 empty] | 14.2857 |  | mM
Used transfer units in absorber |  | 3.6759 | [8 empty] | 0.012303 |  |  | mmol N/mol gas
Concentration of ammonium sulphate, weight % | 20% | 1.5152 | M
Entrainment of ammonium sulphate mg droplets/m3 gas | 20 |  | mg/m3
Entrainment rate |  | 0.24242 | mmol N/s
Ammonia after absorption mmole NH3/mole gas |  | 0.012303 | mmol/mol | [7 empty] | 4 |  | m3/s
due to nonabsorbed NH3, mmol/mol gas |  | 0.010647 | mmol/mol | [7 empty] | 146.422 |  | mol /s
due to entrainment, mmol/mol gas |  | 0.0016557 | mmol/mol
Ammonia conc in gas from stripper, mmol/mol gas |  | 0.48901 | mmol/mol
Equilibrium conc of NH3 above ammonium sulfate sol |  | 1.0685e-06 | mmol/mol | [7 empty] | 0.48573 | [7 empty] | H2SO4
pH value in absorber | 4 | [9 empty] | mmol N/mol gas
Driving conc difference in top of absorber (gas) |  | 0.012302 | mmol/mol |  |  |  | 60 |  | °C | [7 empty] | 7.8673 |  | l/h
Driving conc difference in bottom of absorber (gas) |  | 0.48573 | mmol/mol |  |  |  | 19.9956 |  | mg N/l | [7 empty] | 630.0154 |  | g/m3
Equilibrium conc of NH3 in top of stripper |  | 0.98538 | mmol/mol |  |  |  | 1.4283 |  | mM
NH3 (g) conc in top of stripper |  | 0.49965 | mmol/mol
Driving conc difference in top of stripper (gas) |  | 0.48573 | mmol/mol
Equilibrium conc of NH3 in bottom of stripper |  | 0.066304 | mmol/mol | [5 empty] | Difference: |  |  | -0.67589
Driving conc difference in bottom of stripper (gas) |  | 0.054001 | mmol/mol | [5 empty] | absorber
Available transfer units in stripper | 4
Used transfer units in stripper |  | 2.4797 | [6 empty] | Difference |  |  | 1.5203
pH value after stripper |  | 9.9139 | pH | [5 empty] | stripper
Sulphuric acid consumption in absorber |  | 7.8673 | l/h
Final pH adjustment
pH after adjustment | 7 |  | pH
Sulphuric acid consumption in final pH adjustment |  | 0.69858 | l/h
Note on A38: Choose 11-11,5
Stripper
Precipitation
Sedimentation
Sand filter
Carbon filter
Heat exch.
Heater.
NH3 Stripper
NH3 Absorber